## Metering Statement
Schedule 6 Meter Statement
Example company name here
CMU123A
(a) | Single Line Diagram – to determine that the Metering System is at the Meter Point and to measure the Metered Volume of the CMU. The single line diagram must show all CMU components and all connections to the Total System, as applicable. | see "SLD - Example.pdf"
(b) | CMU Metering Site details (to include the following):
| (i) CMU ID; | CMU123
| (ii) Circuit name (if applicable); | A15
| (iii) Confirmation that the CMU is either a Generating CMU or a Demand Side Response CMU; | Demand Side Response CMU
| (iv) Type of site; | Lighting load
| (v) Site address; | 123, Capacity market road, London NW1 1BC
| (vi) Site contact details; and | Please contact Capacity Provider: John Example +02012 345678 john.example@capacitymarket.com
| (vii) Arrangements for Site Audit | Site induction required
| (viii) Type of Metering Configuration Solution used and where this is Balancing Services the relevant Balancing Services Agreement. | Bespoke
| (ix) The rated output of any Generating Unit (kW or MW) or the rated capacity of the circuit (kVA or MVA), as applicable. [CP301] | 2500 kW each
(c) | Metering Technical details (to include the following):
| (i) Meter Point Administration Numbers or Metering System Identifier(s); | ACMU123A15
| (ii) Meter serial numbers; | Data Provided in "Meter technical details" folder in data file
| (iii) Outstation ID; | Data Provided in "Meter technical details" folder in data file
| (iv) number of channels; | Data Provided in "Meter technical details" folder in data file
| (v) measurement quantity ID; | Data Provided in "Meter technical details" folder in data file
| (vi) Meter and pulse multipliers; | Data Provided in "Meter technical details" folder in data file
| (viii) Current and voltage transformer ratios applied; | Data Provided in "Meter technical details" folder in data file
| (ix) Communications numbers and confirm method for remote communication; | Data Provided in "Meter technical details" folder in data file
| (x) Metering dispensations for the Metering Site (if applicable); | Data Provided in "Meter technical details" folder in data file
| (xi) Complex Site Supplementary Form (if applicable). In respect of an SMRS registered CMU: the D0268, in respect of a CMRS CMU: the BSCP20/4.3a, b and c forms and in respect of a Metering Site using the Bespoke Metering Configuration Solution the Key Meter Technical Details form; and | Data Provided in "Meter technical details" folder in data file
| (xii) If the CMU is identical to the BM Unit, the completed Aggregation Rule Form BSCP75/4.2. If the CMU is different from the BM Unit, the Capacity Provider must provide details of the metered data values to be aggregated to the appropriate Metered Volume for the CMU. | Not Applicable
| (xiii) Where multiple Metering Systems are used the aggregation rule 4 for the CMU, GeneratingUnit or DSR CMU Component should be provided unless provided under (c)(xi) or (c)(xii). [CP301] | Not Applicable
(d) | In respect of a CMU not using a Meter that measures on a half hourly basis, the Capacity Provider must provide the following metering information:
| (i) Technical specification of the device providing instantaneous metering values; | Same for all four meters: "CMU111 Meter - Technical Specifications.pdf"
| (ii) A calibration test certificate for the device listed in paragraph (d)(i) above; | "CMU123A - Main Meter - Calibration Cert - 123456789.pdf"; "CMU123A - Check Meter - Calibration Cert - 123456790.pdf";
| (iii) Ratios of any connected instrument transformers; | CT 400/1 VT 11000/100
| (iv) Details of the Settlement Instation; and | Individual on-site meters record cumulative kWh energy readings timestamped in UTC in for each 30 minute settlement period. The 30 minute data is queried from the local SCADA system for the relevant day and converted into the standard CSV format, and will be submitted to EMRS via SFTP on a monthly basis or more frequently as requested. See "CMU123AMAIN_AE_16_4_2025.csv"
| (v) Confirmation of the method used of converting to half hourly data to submit to the CM Settlement Body. | See section d(iv).
(e) | Data Provision
A Capacity Provider must confirm:
| (i) the method it proposes to use to submit data to the CM Settlement Body; and | 1. The lighting metering data shall be submitted under the 'self-submission' pathway. 2. Metered data will be provided to EMRS in the defined file format in accordance with Elexon working practice 'WP195 - Capacity Market and CFD Metered Data' version 1.0 . 3. An example of the data file is provided for the commissioning test in the data file. 4. Data is submitted on a weekly basis via SFTP.
| (ii) if applicable, the contact details of the relevant Half Hourly Data Aggregators or Half Hourly Data Collectors to enable the CM Settlement Body to confirm the Metering Technical details provided by the Capacity Provider at paragraph (c) above, match those held by the Half Hourly Data Aggregators or Half Hourly Data Collectors. | Half-hourly meter data can be provided by email on a daily, weekly or monthly basis,
| (iii) Where data is submitted using the method set out in 14.2.7 an example of the comma separated value file in the format specified by the CM Settlement Body must be provided. [CP301] | Half-hourly meter data can be provided by email on a daily, weekly or monthly basis,
(f) | Time Synchronisation
| A Capacity Provider must provide a statement detailing how the time of the meters or Settlement Instation used is synchronised to UTC. [CP301] | Automated via Data collector.
(g) | Security
| A Capacity Provider must submit a detailed description of their security arrangements, including, where applicable, details of any sealed or padlocked hardware and password protected IT software. | The meter system is installed within the switchgear room for the site which is kept locked at all times. The meter system is sealed and operated by The company Ltd. Meter data is made available to "The company" automated email form the secure metering portal.
(h) | Testing Facilities
| A Capacity Provider must submit a detailed description of the testing facilities and fusing arrangements for the Meters. | 1. The meter cabinet is located in the HV sub close to the switchgear being monitored. The meter cabinet is fitted with a set of Wago CoP3 test terminals for each meter 2. Meter testing facilities (test block) and fusing arrangements are mounted inside the metering cabinet. 2A fuses.
(i) | Installation Date
| A Capacity Provider must confirm the date that the Metering System was installed and commissioned to enable the CM Settlement Body to verify compliance with the relevant Governing Documents, as applicable, at that time. If the date of installation and commissioning is unknown, the Capacity Provider must undertake a new commissioning test. | Current transformers: 17/09/2025 Meters: 15/10/2025
(j) | Instrument Transformers
| A Capacity Provider must provide evidence to enable the CM Settlement Body to determine the relevant transformers are of the correct accuracy class and that any errors are within the allowed limits of that class. The evidence may be either: (i) the manufacturer’s test certificates; or (ii) technical information from the manufacturer confirming the ratio(s), rated burden, accuracy class and the errors for the same type and configuration of Instrument Transformers as that installed. Relevant technical information should include, as applicable: (a) the manufacturer’s test certificate for an equivalent transformer; or (b) an error from the National Measurement Transformer Database; or (c) the range of errors from the design characteristics of the transformer as specified in the design specification of a transformer. [CP301] | Ratio CTs 400/1A Rated burden CTs 5 VA Accuracy Class CTs Class 0.5S L-1 CT serial number 3S.2188-007 L-2 CT serial number 3S.2188-008 L-3 CT serial number 3S.2188-009 Ratio VTs 11000/100 Rated burden VTs 10VA Accuracy Class VTs Class 0.2 VT (Red -Yellow) serial number 1VLT5217007617 VT (Yellow-Blue) serial number 1VLT5217007618 VT (Blue-Red) serial number 1VLT5217007619
(k) | Power Transformers
| A Capacity Provider must submit a copy of the evidence of the Power Transformer losses used as part of their approved dispensation which accounts for transformer losses where the installed metering is not at the defined Meter Point and there is a power transformer between the two points. This evidence should include, as applicable: (i) the manufacturer’s Power Transformer Test Certificate for the installed Power Transformer; or (ii) the manufacturer’s Power Transformer Test Certificate for a Power Transformer of the same type as that installed; or (iii) an average figure approved for use under the dispensation. [CP301] | Not Applicable
(l) | Meters
A Capacity Provider must provide either:
| (i) A Manufacturers test certificate; | Provided in the data file
| (ii) A letter from the manufacturer confirming the typical errors of the device; or | Not Applicable
| (iii) A calibration test certificate tested at the calibration testing points set out in the table below performed by a third party | Not Applicable
| (iv) For non-integral Outstation meters a calibration test certificate that confirms the errors of the meter. [CP301] | Not Applicable
(m) | Instrument Transformer Burdens
A Capacity Provider must provide either:
| (i) a measurement of the burden connected to the current and voltage transformer; or | L-1 CT actual/estimated burden (VA) 1.06 VA – L-2 CT actual/estimated burden (VA) n/a L-3 CT actual/estimated burden (VA) 1.06 VA – VT (Red -Yellow) actual/estimated burden (VA) 6.06 VA – VT (Yellow-Blue) actual/estimated burden (VA) 6.06 VA – VT (Blue-Red) actual/estimated burden (VA) 6.06 VA –
| (ii) a calculated estimate of the burden connected to the current and voltage transformer so as to determine that these connected burdens are less than the rated burden of the transformer. | Not Applicable
| In the case of (ii), a Capacity Provider must also submit a justification as to why it was not possible to provide a measurement of the burden connected to the current and voltage transformer. | Not Applicable
(n) | Commissioning requirements
| Measurement Transformers Commissioning | Evidence for commissioning of measurement transformers is provided in accordance to Option 5A as outlined in the EMRS G20 guidance document on Metering Statements. Provided in the data file See the following meter configuration reports exported directly from the meter: Main: "CMU123A GEN Main Meter Configuration Report.txt" Check: "CMU123A GEN Check Meter Configuration Report.txt"
| Meter Commissioning | Meter commissioning was done by comparing secondary current/voltage measured with a handheld instrument with Meter primary values. Recorded values from the commissioning test are included in the following commissioning documents: Provided in the data file Main: "GC2540A GEN Main Meter Commissioning.pdf" Check: "GC2540A GEN Check Meter Commissioning.pdf"
| Meter Proving | Provided in the data file
(o) | Transformer Loss Compensations
| In the event that transformer error or loss compensation has been applied to the metering, a Capacity Provider must provide evidence of the compensation calculation. The evidence provided can be for the measurement of transformer errors only or, in the case of a dispensation, Power Transformer Losses. The evidence should include as a minimum the compensation figures programmed into the Meter or incorporated into the Aggregation Rule (as applicable). [CP301] | Not applicable
(p) | Cable and Overhead Line Loss Compensations
| In the event that cable and overhead line loss compensation has been applied to the metering, a Capacity Provider must provide evidence of the compensation calculation. The evidence should include as a minimum the compensation figures programmed into the Meter or incorporated into the Aggregation Rule (as applicable). [CP301] | Not applicable
(q) | Electrical Losses Factor
| A Capacity Provider using the Balancing Services Metering Configuration Solution or the Bespoke Metering Configuration Solution operating on an Unlicensed Network must provide, where applicable, a copy of the methodology statement justifying the Unlicensed Network operator’s calculations of electrical losses from the CMU component connection point to the Boundary Point of the Unlicensed Network with the Total System. The evidence should include as a minimum the compensation figures programmed into the Meter or incorporated into the Aggregation Rule (as applicable). [CP301] | Not applicable
(r) | Declaration
| The Directors of the Capacity Provider must certify that the information contained in and enclosed with the Metering Statement, is, at the date of submission and to the best of their knowledge, information and belief, true, complete and accurate in all material respects. | See "CMU123 Metering Statement Declaration.pdf"